## Calcualtions
Inputs |  |  | Converter transformer short circuit power [%] | 15 |  | zbase | 1600 | Losses check:
Power rating [MW] | 3200 |  | X/R ratio | 35 |  | zbase dc | 2756.25 | utilization in pu | utilization in MW | losses in mMW | losses in %
Voltage AC [kV] | 400 |  | Reactor short circuit ratio [%] | 7.5 |  |  |  | 0.1 | 320 | 4.7626 | 0.14883
Voltage DC [kV] | 525 |  | X/R ratio | 30 |  |  |  | 0.2 | 640 | 6.2186 | 0.19433
Length in km | 4000 |  | Z transformer [Ohm] | 7.5 |  |  |  | 0.3 | 960 | 7.8986 | 0.24683
Outputs |  |  | X transformer [Ohm] | 7.4969 | 0.023864 |  |  | 0.4 | 1280 | 9.8026 | 0.30633
R transformer [pu] | 0.00013387 |  | R transformer [Ohm] | 0.2142 |  |  |  | 0.5 | 1600 | 11.9306 | 0.37283
X transformer [pu] | 0.0046856 |  | Z reactor [Ohm] | 3.75 |  |  |  | 0.6 | 1920 | 14.2826 | 0.44633
B filter | 15.0796 | Not reqiored for VSC & MMC | X reactor [Ohm] | 3.7479 | 0.01193 |  |  | 0.7 | 2240 | 16.8586 | 0.52683
R reactance [pu] | 7.8082e-05 |  | R reactor [Ohm] | 0.12493 |  |  |  | 0.8 | 2560 | 19.6586 | 0.61433
X reactance [pu] | 0.0023424 | [6 empty] | 0.9 | 2880 | 22.6826 | 0.70883
loss a MW | 3.5306 | [6 empty] | 1 | 3200 | 25.9306 | 0.81033
loss b V/A | 2.4249
loss c Ohm | 0.00175 |  | DC current [A] | 3047.619
|  |  | circuits | 1
OHL R in pu | 0.018759 |  | bundles | 3
Cable R pu | 0.14626 | aluminum | current per conductor | 1015.873
Cable R pu | 0.0067669 | copper | OHL Cross-section needed | 489.6162
|  |  | Cable cross section needed | 3817.4069
|  |  | Filter capacitor | 3e-05 | {} according to | 10.1109/TPWRD.2014.2340870
|  |  | Frequency | 50

## Cable - OHL loss data
ACSR conductor data
Codeword | Size (sqmm) | Stranding (Al/Steel) | Diameter (mm) |  | Ampacity | Approx. overall diameter (mm)
|  |  | Steel wire | Al wire
Turkey | 15.52 | 6/1 | 1.6789 | 1.6789 | 110 | 5.04
Swan | 24.71 | 6/1 | 2.1184 | 2.1184 | 145 | 6.36
Swanate | 26.47 | 7/1 | 2.6137 | 1.9609 | 145 | 6.53
Sparrow | 39.19 | 6/1 | 2.6721 | 2.6721 | 195 | 8.01
Spa rate | 42.09 | 7/1 | 3.2995 | 2.474 | 195 | 8.24
Robin | 49.48 | 6/1 | 2.9997 | 2.9997 | 200 | 9
Raven | 62.44 | 6/1 | 3.3706 | 3.3706 | 255 | 10.11
Quail | 78.55 | 6/1 | 3.7821 | 3.7821 | 295 | 11.34
Pigeon | 99.31 | 6/1 | 4.2469 | 4.2469 | 340 | 12.75
Penguin | 125.1 | 6/1 | 4.7701 | 4.7701 | 390 | 14.31
Waxwing | 142.5 | 18/1 | 3.0912 | 3.0912 | 480 | 15.45
Partridge | 156.9 | 26/7 | 2.0015 | 2.573 | 490 | 16.28
Merlin | 179.7 | 18/1 | 3.4722 | 3.4722 | 560 | 17.35
Linnet | 198.4 | 26/7 | 2.2454 | 2.888 | 570 | 18.31
Oriole | 210.3 | 30/7 | 2.6899 | 2.6899 | 575 | 18.83
Chickadee | 212.1 | 18/1 | 3.7744 | 3.7744 | 620 | 18.85
Ibis | 234 | 26/7 | 2.4409 | 3.1394 | 635 | 19.88
Pelican | 255.8 | 18/1 | 4.1351 | 4.1351 | 700 | 20.7
Flicker | 273 | 24/7 | 2.3876 | 3.5814 | 710 | 21.49
Hawk | 281.1 | 26/7 | 2.6746 | 3.4392 | 715 | 21.77
Hen | 297.6 | 30/7 | 3.2029 | 3.2029 | 725 | 22.4
Osprey | 298.2 | 18/1 | 4.4653 | 4.4653 | 775 | 22.35
Parakeet | 318.9 | 24/7 | 2.5781 | 3.8684 | 785 | 23.22
Dove | 328.5 | 26/7 | 2.8905 | 3.716 | 790 | 23.55
Rook | 365 | 24/7 | 2.7559 | 4.1351 | 855 | 24.84
Grosbeak | 374.3 | 26/7 | 3.0886 | 3.9726 | 860 | 25.15
Tern | 431.6 | 45/7 | 2.2504 | 3.3757 | 970 | 27.03
Drake | 468 | 26/7 | 3.4544 | 4.4425 | 995 | 28.11
Rail | 517.3 | 45/7 | 2.4663 | 3.6982 | 1090 | 29.61
Cardinal | 547.3 | 54/7 | 3.3757 | 3.3757 | 1095 | 30.42
Curlew | 593.6 | 54/7 | 3.5128 | 3.5128 | 1150 | 31.62
Bluejay | 604.4 | 45/7 | 2.6645 | 3.9954 | 1205 | 31.98
Bittern | 689.1 | 45/7 | 2.8473 | 4.2672 | 1310 | 34.16
Lapwing | 859.8 | 45/7 | 3.1826 | 4.7752 | 1505 | 38.2
Bluebird | 1092.28 | 84/19 | 2.4409 | 4.0691 | 1815 | 44.76
Submarine |  |  |  | Land
Area | Ampacity |  |  | Area | Ampacity
Cross-section | Close laying | Spaced laying |  | Cross-section | Close laying | Spaced laying
[mm2] | [A] | [A] |  | [mm2] | [A] | [A]
95 | 343 | 404 |  | 95 | 344 | 413.3333
120 | 392 | 463 |  | 120 | 392 | 476
150 | 441 | 523 |  | 150 | 440 | 536
185 | 500 | 596 |  | 185 | 498.6667 | 610.6667
240 | 583 | 697 |  | 240 | 576 | 710.6667
300 | 662 | 797 |  | 300 | 656 | 814.6667
400 | 765 | 922 |  | 400 | 753.3333 | 940
500 | 883 | 1072 |  | 500 | 878.6667 | 1088
630 | 1023 | 1246 |  | 630 | 969.3333 | 1285.3333 | Losses
800 | 1175 | 1438 |  | 800 | 1169.3333 | 1458.6667 | 50 | 0.4 | 0.125 | 0.0056
1000 | 1335 | 1644 |  | 1000 | 1334.6667 | 1669.3333 | 100 | 0.8 | 0.25 | 0.0056
1200 | 1458 | 1791 |  | 1200 | 1461.3333 | 1828 | 150 | 1.3 | 0.375 | 0.0060667
1400 | 1594 | 1962 |  | 1400 | 1614.6667 | 2022.6667 | 200 | 1.8 | 0.5 | 0.0063
1600 | 1720 | 2123 |  | 1600 | 1721.3333 | 2161.3333 | 250 | 2.45 | 0.625 | 0.00686
1800 | 1830 | 2265 |  | 1800 | 1860 | 2336 | 300 | 3.05 | 0.75 | 0.0071167
2000 | 1953 | 2407 |  | 2000 | 1976 | 2488 | 350 | 3.75 | 0.875 | 0.0075
2200 | 2062 | 2540 |  | 2200 | 2094.6667 | 2617.3333 | 400 | 4.5 | 1 | 0.007875
2400 | 2170 | 2678 |  | 2400 | 2202.6667 | 2754.6667
2600 | 2275 | 2814 |  | 2600 | 2305.3333 | 2888
2800 | 2373 | 2937 |  | 2800 | 2408 | 3017.3333
3000 | 2473 | 3066 |  | 3000 | 2504 | 3141.3333
Note on A41: ampacity values are taken from: HVDC Light Cables-Submarine and land power cables, 2006